## IO Address List
NovaBio Therapeutics — OPC-UA I/O Address List ¦ NVBT-IO-ADDR-2026-001 ¦ Server: opc.tcp://10.10.1.5:4840 ¦ Namespace: ns=2
Suite | Tag ID | Description | Signal | Eng. Range | OPC-UA Node ID | FrameworX UNS Path
USP-SEED
USP-SEED | TT-S01 | Vessel temperature — Seed | AI | 0-100 °C | ns=2;s=NovaBio.USP.Seed.TT_S01.PV | NovaBio/Cambridge/Mfg/USP_SEED/BR_S20/Temperature
USP-SEED | pHT-S01 | Vessel pH — Seed | AI | 0-14 | ns=2;s=NovaBio.USP.Seed.pHT_S01.PV | NovaBio/Cambridge/Mfg/USP_SEED/BR_S20/pH
USP-SEED | DOT-S01 | Dissolved oxygen — Seed | AI | 0-200 %sat | ns=2;s=NovaBio.USP.Seed.DOT_S01.PV | NovaBio/Cambridge/Mfg/USP_SEED/BR_S20/DO
USP-PROD
USP-PROD | TT-PA02 | Vessel temperature — Train A | AI | 0-100 °C | ns=2;s=NovaBio.USP.Prod.TT_PA02.PV | NovaBio/Cambridge/Mfg/USP_PROD/BR_PA/Temperature
USP-PROD | pHT-PA01 | Vessel pH — Train A | AI | 0-14 | ns=2;s=NovaBio.USP.Prod.pHT_PA01.PV | NovaBio/Cambridge/Mfg/USP_PROD/BR_PA/pH
USP-PROD | DOT-PA01 | Dissolved oxygen — Train A | AI | 0-200 %sat | ns=2;s=NovaBio.USP.Prod.DOT_PA01.PV | NovaBio/Cambridge/Mfg/USP_PROD/BR_PA/DO
USP-PROD | AGT-PA01 | Agitator speed — Train A | AI | 0-150 RPM | ns=2;s=NovaBio.USP.Prod.AGT_PA01.PV | NovaBio/Cambridge/Mfg/USP_PROD/BR_PA/AgitatorSpeed
USP-PROD | FT-PA01 | Harvest flow — Train A | AI | 0-500 L/hr | ns=2;s=NovaBio.USP.Prod.FT_PA01.PV | NovaBio/Cambridge/Mfg/USP_PROD/BR_PA/HarvestFlow
USP-PROD | TT-PB02 | Vessel temperature — Train B | AI | 0-100 °C | ns=2;s=NovaBio.USP.Prod.TT_PB02.PV | NovaBio/Cambridge/Mfg/USP_PROD/BR_PB/Temperature
USP-PROD | pHT-PB01 | Vessel pH — Train B | AI | 0-14 | ns=2;s=NovaBio.USP.Prod.pHT_PB01.PV | NovaBio/Cambridge/Mfg/USP_PROD/BR_PB/pH
DSP-HARV
DSP-HARV | PT-H01 | Centrifuge back-pressure | AI | 0-6 bar | ns=2;s=NovaBio.DSP.Harv.PT_H01.PV | NovaBio/Cambridge/Mfg/DSP_HARV/CF_H01/BackPressure
DSP-HARV | TT-H01 | Centrifuge bowl temperature | AI | 0-80 °C | ns=2;s=NovaBio.DSP.Harv.TT_H01.PV | NovaBio/Cambridge/Mfg/DSP_HARV/CF_H01/BowlTemp
DSP-HARV | CON-H01 | TFF permeate conductivity | AI | 0-200 mS/cm | ns=2;s=NovaBio.DSP.Harv.CON_H01.PV | NovaBio/Cambridge/Mfg/DSP_HARV/TFF_H01/Conductivity
DSP-CHROM
DSP-CHROM | UV-C01 | UV absorbance 280 nm | AI | 0-3 AU | ns=2;s=NovaBio.DSP.Chrom.UV_C01.PV | NovaBio/Cambridge/Mfg/DSP_CHROM/UV/Absorbance
DSP-CHROM | PT-C01 | Column inlet pressure | AI | 0-5 bar | ns=2;s=NovaBio.DSP.Chrom.PT_C01.PV | NovaBio/Cambridge/Mfg/DSP_CHROM/InletPressure
DSP-FORM
DSP-FORM | WT-F01 | Retentate net weight | AI | 0-500 kg | ns=2;s=NovaBio.DSP.Form.WT_F01.PV | NovaBio/Cambridge/Mfg/DSP_FORM/TFF_F01/Weight
DSP-FORM | TT-F01 | Product temperature | AI | 0-25 °C | ns=2;s=NovaBio.DSP.Form.TT_F01.PV | NovaBio/Cambridge/Mfg/DSP_FORM/TFF_F01/Temperature
UTIL-CIP
UTIL-CIP | TT-U03 | Clean steam temperature (SIP) | AI | 0-150 °C | ns=2;s=NovaBio.Util.CIP.TT_U03.PV | NovaBio/Cambridge/Mfg/UTIL_CIP/SteamTemp
UTIL-CIP | CIP-U01 | CIP Skid A phase status | DI | — | ns=2;s=NovaBio.Util.CIP.CIP_U01.Phase | NovaBio/Cambridge/Mfg/UTIL_CIP/CIP_U01/Phase
UTIL-WFI
UTIL-WFI | TT-U02 | WFI loop temperature | AI | 0-100 °C | ns=2;s=NovaBio.Util.WFI.TT_U02.PV | NovaBio/Cambridge/Mfg/UTIL_WFI/LoopTemp
UTIL-WFI | CON-U02 | WFI conductivity | AI | 0-5 µS/cm | ns=2;s=NovaBio.Util.WFI.CON_U02.PV | NovaBio/Cambridge/Mfg/UTIL_WFI/Conductivity

## Connection Config
NovaBio Therapeutics — Device & Protocol Connection Configuration
Parameter | Value | Notes
Protocol | OPC-UA | Connection from FrameworX to DeltaV DCS
Device / PLC | Emerson DeltaV v14.3 DCS | Main plant controller
Device IP Address | 10.10.1.5 | Static IP — plant network segment
OPC-UA Endpoint URL | opc.tcp://10.10.1.5:4840 | Default DeltaV OPC-UA server port
Namespace Index | ns=2 | NovaBio process namespace on DeltaV server
FrameworX Device Name | NovaBio_DeltaV | Device object name in FrameworX solution
UNS Root Path | NovaBio/Cambridge/Mfg/ | ISA-95 hierarchy root — all tags publish here
Analog Sub. Rate | 1000 ms (1 Hz) | All AI/AO tags
Digital Sub. Rate | On-change | DI/DO status and phase tags
Security Mode | SignAndEncrypt | Production environment
Security Policy | Basic256Sha256 | Certificate-based authentication
Service Account | fxopc_svc | OPC-UA username credential in FrameworX